## Efficiency Calculator
Efficiency Comparison Calculator
Operating Hrs/ year | 8000
Energy Cost | 7 | (Cents per KW Hour)
HP | 450
RPM | 3600
Motor #1 (Premium Efficiency) |  |  | Motor Cost | 22320 |  |  | Description: | Toshiba EQPIII - 507USS - ODP
Eff'y @ F/L (%) | 96.2%
Eff'y @ 3/4 (%) | 96.5%
Eff'y @ 1/2 (%) | 96.5%
Motor #2 (Comparison Motor) |  |  | Motor Cost | 17103 |  |  | Description: | Toshiba High Efficiency - 505USS - ODP
Eff'y @ F/L (%) | 94.4%
Eff'y @ 3/4 (%) | 94.3%
Eff'y @ 1/2 (%) | 92.8% | [6 empty] | Energy Savings versus Years of operation
[8 empty] | 1 | 2 | 3 | 4 | 5
|  |  | Delta Cost | 5217 | Difference in |  |  | 3726 | 7452 | 11178 | 14904 | 18630
[5 empty] | Operating |  |  | 3408 | 6816 | 10224 | 13632 | 17040
Motor #1 |  |  | Motor #2 |  | Costs per year |  |  | 3884 | 7768 | 11652 | 15536 | 19420
Energy cost @ F/L | 195418 |  | Energy cost @ F/L | 199144 |  | 3726 |  | 6 | 7 | 8 | 9 | 10
Energy cost @ 3/4 | 146108 |  | Energy cost @ 3/4 | 149516 |  | 3408 |  | 22356 | 26082 | 29808 | 33534 | 37260
Energy cost @ 1/2 | 97405 |  | Energy cost @ 1/2 | 101289 |  | 3884 |  | 20448 | 23856 | 27264 | 30672 | 34080
[8 empty] | 23304 | 27188 | 31072 | 34956 | 38840

## EQPIII Data
TOSHIBA EQPIII SERIES MOTOR DATA
Note 900RPM Motor Data is Toshiba High Efficiency Series, not EQPIII
Rated | Full |  | Eff'y | Eff'y | Eff'y
HP: | Load | Frame | @1.0 | @0.75 | @O.5
| RPM | (#) | (%) | (%) | (%)
1 | 862 | 182T | 74 | 76.1 | 71.5
| 1152 | 145T | 82.4 | 82 | 78
| 1749 | 143T | 85.7 | 86.1 | 84.1
| 3526 | 143T | 83.3 | 80.5 | 78.8
1.5 | 866 | 184T | 77 | 76 | 71.4
| 1168 | 182T | 86.4 | 86.1 | 84.1
| 1740 | 145T | 86.9 | 87.1 | 85.7
| 3489 | 143T | 85.4 | 84.9 | 82.4
2 | 863 | 213T | 80 | 80.2 | 77.4
| 1172 | 184T | 88.4 | 87.7 | 85.3
| 1733 | 145T | 86.8 | 87.3 | 86.2
| 3499 | 145T | 86.4 | 86.3 | 84.4
3 | 864 | 215T | 82.5 | 82 | 79.2
| 1167 | 213T | 90.3 | 91 | 89.9
| 1754 | 182T | 89.5 | 89.7 | 88.6
| 3509 | 182T | 88.8 | 88.9 | 87.6
5 | 874 | 254T | 86.5 | 87.3 | 86
| 1165 | 215T | 90.1 | 89.7 | 87.4
| 1737 | 184T | 88.4 | 89.7 | 89.4
| 3502 | 184T | 89 | 89.1 | 87.7
7.5 | 878 | 256T | 87.5 | 88 | 87.3
| 1179 | 254T | 92 | 91.8 | 90.6
| 1752 | 213T | 90.9 | 91.2 | 90.3
| 3515 | 213T | 90.5 | 90.3 | 89
10 | 879 | 284T | 88.5 | 89.1 | 87.5
| 1176 | 256T | 92.5 | 92.8 | 92
| 1746 | 215T | 90.9 | 91.3 | 90.4
| 3510 | 215T | 90.3 | 90 | 88
15 | 877 | 286T | 89.5 | 89.3 | 87.9
| 1173 | 284T | 92.3 | 92.5 | 92
| 1774 | 254T | 92.4 | 92.6 | 91.8
| 3533 | 254T | 91.6 | 92 | 91.6
20 | 879 | 324T | 89.5 | 89.9 | 88.9
| 1170 | 286T | 92.3 | 92.6 | 92.2
| 1772 | 256T | 93.1 | 93.4 | 93
| 3535 | 256T | 92.5 | 93.2 | 93.2
25 | 881 | 326T | 91 | 90.9 | 88.7
| 1175 | 324T | 92.9 | 93.5 | 93
| 1770 | 284T | 93.5 | 93.7 | 93.1
| 3529 | 284TS | 92.4 | 93 | 92
30 | 879 | 364T | 91 | 91 | 89.5
| 1177 | 326T | 93.6 | 94 | 93.7
| 1770 | 286T | 93.4 | 93.6 | 93
| 3524 | 286TS | 92.4 | 93.1 | 92.1
40 | 877 | 365T | 91 | 91.7 | 91.3
| 1176 | 364T | 94 | 94.6 | 94.5
| 1770 | 324T | 94 | 94.4 | 94.1
| 3535 | 324TS | 93.1 | 93.4 | 92.8
50 | 879 | 404T | 91 | 92 | 91.3
| 1175 | 365T | 93.6 | 94.4 | 94.3
| 1771 | 326T | 94 | 94.2 | 93.9
| 3533 | 326TS | 93 | 93.3 | 92.6
60 | 880 | 405T | 91 | 91.3 | 91.3
| 1187 | 404T | 95 | 95.1 | 94.6
| 1777 | 364T | 95.1 | 95.2 | 94.6
| 3547 | 364TS | 93.8 | 94 | 93.7
75 | 882 | 444T | 91.7 | 92.3 | 92
| 1186 | 405T | 94.9 | 95.1 | 94.5
| 1775 | 365T | 95.3 | 95.5 | 95
| 3540 | 365TS | 93.5 | 93.8 | 93.4
100 | 881 | 445T | 92.4 | 93 | 92.8
| 1183 | 444T | 95.5 | 95.7 | 95.2
| 1776 | 405T | 95.4 | 95.6 | 95.3
| 3557 | 405TS | 95 | 95 | 94.8
125 | 885 | 505UZ | 93.6 | 93.8 | 93.3
| 1186 | 445T | 95.5 | 95.6 | 95.5
| 1785 | 444T | 95.7 | 95.7 | 95
| 3575 | 444TS | 95.3 | 95.2 | 94.8
150 | 884 | 505UZ | 93.6 | 93.7 | 93.5
| 1184 | 447T | 95.8 | 96.2 | 96.1
| 1784 | 445T | 95.7 | 95.5 | 94.8
| 3577 | 445TS | 95.7 | 95.7 | 95.2
200 | 888 | N587UZ | 93 | 94.5 | 94.2
| 1188 | 505UZ | 95.8 | 96.1 | 96
| 1185 | 449TZ | 95.4
| 1784 | 447T | 96.1 | 96.1 | 95.7
| 3576 | 447TSS | 96 | 95.9 | 95.3
250 | 887 | N587UZ | 93.6 | 94 | 93.7
| 1188 | 5010UZ | 95.8 | 95.8 | 95.7
| 1788 | 505UZ | 96.2 | 95.9 | 95
| 3582 | 5010USS | 95 | 95.2 | 95
300 | 1188 | 5010UZ | 96.2 | 96 | 95.9
| 1788 | 5010UZ | 96.5 | 96.6 | 96.1
| 3582 | 5010US | 95.8 | 96 | 95.4
350 | 1185 | 5010US | 95.8
| 1788 | 5010US | 96.2 | 96.2 | 95.5
400 | 1788 | 5010US | 96.2 | 96 | 95.3

## Epact Data
TOSHIBA EPACT SERIES MOTOR DATA
Rated | Full |  | Eff'y | Eff'y | Eff'y
HP: | Load | Frame | @1.0 | @0.75 | @O.5
| RPM | (#) | (%) | (%) | (%)
1 | 1725 | 143T | 83.4 | 81.7 | 78.3
| 1149 | 145T | 81.3 | 81.2 | 78.6
1.5 | 3485 | 143T | 82.5 | 83.2 | 82.2
| 1725 | 145T | 84 | 83.5 | 80.6
| 1165 | 182T | 85.6 | 84 | 82
2 | 3477 | 145T | 84.1 | 84.2 | 83.2
| 1739 | 145T | 86.22 | 86.93 | 85.64
| 1165 | 184T | 86.6 | 86.5 | 84.4
3 | 3485 | 184T | 85.5 | 86.5 | 86.3
| 1735 | 182T | 87.7 | 87.7 | 85.5
| 1160 | 213T | 87.7 | 88.7 | 88.6
5 | 3472 | 184T | 87.7 | 88.9 | 88.6
| 1726 | 184T | 87.83 | 89.24 | 89.51
| 1153 | 215T | 88 | 89 | 88.8
7.5 | 3488 | 213T | 88.7 | 89.1 | 88.3
| 1745 | 213T | 89.6 | 89.6 | 88.1
| 1165 | 254T | 89.8 | 90.5 | 90.2
10 | 3492 | 215T | 90 | 90.4 | 89.6
| 1740 | 215T | 89.6 | 90.8 | 91.17
| 1167 | 256T | 89.7 | 90.4 | 90.2
15 | 3520 | 254T | 90.4 | 91 | 90.5
| 1769 | 254T | 91 | 91.6 | 91.2
| 1160 | 284T | 90.3 | 91.4 | 91.6
20 | 3513 | 256T | 90.7 | 91.2 | 90.7
| 1763 | 256T | 91.2 | 92.2 | 92.4
| 1159 | 286T | 90.5 | 91.5 | 91.6
25 | 3515 | 284TS | 91.2 | 92.1 | 92.2
| 1767 | 284TS | 92.5 | 93 | 92.8
| 1170 | 324T | 91.9 | 91.7 | 90.4
30 | 3513 | 286TS | 91.2 | 92.1 | 92.2
| 1767 | 286T | 92.6 | 93.4 | 93.2
| 1172 | 326T | 92.11 | 93 | 92.97
40 | 3510 | 324TS | 91.9 | 92.5 | 92.2
| 1763 | 324T | 93 | 93.4 | 93.1
| 1170 | 364T | 93.2 | 93.3 | 92.6
50 | 3520 | 326TS | 92.8 | 93.4 | 93.3
| 1763 | 326T | 93.2 | 93.5 | 93.5
| 1173 | 365T | 93.47 | 94.27 | 94.44
60 | 3538 | 364TS | 93.6 | 93.7 | 93
| 1773 | 364T | 94 | 94.2 | 94
| 1180 | 404T | 93.8 | 93.3 | 92
75 | 3543 | 365TS | 93.5 | 93.4 | 92.4
| 1773 | 365T | 94.4 | 94.6 | 94.3
| 1184 | 405T | 94.13 | 94.47 | 94.13
100 | 3555 | 405TS | 93.89 | 93.85 | 92.95
| 1771 | 405T | 94.49 | 94.82 | 94.47
| 1180 | 444T | 94.5 | 94.3 | 93.1
125 | 3565 | 444TS | 94.5 | 93.8 | 92
| 1780 | 444T | 94.8 | 94.3 | 93
| 1180 | 445T | 94.7 | 94.5 | 93.5
150 | 3565 | 445TS | 95.1 | 94.4 | 92.8
| 1780 | 445T | 95.1 | 94.7 | 93.5
| 1183 | 447TZ | 95.25 | 95.61 | 95.44
200 | 3571 | 447TSS | 95.16 | 95.18 | 94.51
| 1781 | 447TZ | 95.79 | 95.75 | 95.13
| 1189 | 505UZ | 96.18 | 96.35 | 96.04

## Calculations
Formula: HP *746W/1000*Hours*cost/KWHr/100/Eff'y
195418
146108
97405
199144
149516
101289